Specification For Paddlewheel Flow Sensor

- Sensor shall be capable of sensing flow in either direction ( bi-directional).

- The flow sensor shall be insertion paddlewheel, with an electrical output signal proportional to flow velocity over a range of 0.3-20 feet per second.  The output signal shall be an open-collector transistor pulse.

- Signal transmission lengths shall be capable of distances up to 1000 feet.

- Sensor shall operate with a power input of 3.3 - 24 vdc, with a maximum current draw of < 20 mA.

- The sensor shall utilize an Installation Fitting that is factory set to control proper flow sensor insertion depth, and orientate sensor to be parallel with fluid flow.

- With a fully developed flow profile the sensor output shall be linear to ±1% of full range, with a repeatability of ±0.5% of full range, and supplied with a certificate traceable to N.I.S.T.

- Three optional sensor lengths shall allow the flow sensor to install into pipes from 0.5 to 36 inches.

- The sensor body materials shall be glass-filled polypropylene (black) or PVDF (natural).

- The flow sensor shall be equipped with dual o-ring seals.  The elastomeric seals shall be FPM-Viton® (standard) with optional EPDM or FFPM-Kalrez®.

- Rotor pins shall be Titanium (standard for PP), Hastelloy-C or PVDF (standard for PVDF), with optional ceramic, Tantalum, or stainless steel.

- Rotor material shall be black PVDF (standard for PP) or natural PVDF (standard for PVDF) with optional Tefzel® with or without Fluoraloy B® sleeve.

- Sensor shall have option capable of integrally mounting a NEMA-4X Flow Indicating Transmitter with 4-20 mA output.

- The flow sensor shall be a Georg Fischer Signet model 2536 or equal.